Checklist of E/OHS Activities for Laboratory Standard/Chemical Hygiene Plan

Program Contact Person: Jeff Ehmke, CHO

Is the Laboratory Standard/Chemical Hygiene Plan in place? *Yes No N/A*

Is the Plan current?  *Yes No N/A*

Has the Plan been reviewed this school year? *Yes No N/A*

Fume hood was tested on: Feb, 2014.

*(date)*

The results indicate air velocity to be: *satisfactory, unsatisfactory.*

Chemical inventory:

Date of most recent survey: May, 2008

Location of inventory listing: Chemistry Lab

Are Material Safety Data Sheets (MSDSs) located with inventory? *Yes No N/A*

Are the MSDS readily accessible? *Yes No N/A*

Has the DCFL Science Lab Checklist been completed? *Yes No N/A*

Is training for affected personnel complete? *Yes No N/A*

Date(s) of instruction: May, 2007

Roster signed? *Yes No N/A*

Lesson plan outline available with roster? *Yes No N/A*

Status of Emergency Eye Wash/Deluge Shower:

Is flushing conducted weekly? *Yes No N/A*

Is descriptive signage properly posted? *Yes No N/A*

Is flushing activity documented? *Yes No N/A*

# Fume Hood Evaluation

**Inspector : Brian Parrie** **Date 2/14/2014**

**Chemical Hygiene Officer: Jeff Ehmke**

**Hood #1** **Location: Room C-130**

|  |  |  |
| --- | --- | --- |
| **FIELD TEST (lf/min)** | | |
| 130 | 135 | 130 |
| 108 | 100 | 108 |

Pass ٱ Fail (face velocity of 100 lf/min cannot be achieved)

Sash Height:15.5” low power, 20.5” high power

Used as Storage? *Yes No*

Clean? *Yes No*

Comments

**Completed by Brian Parrie**  **Date 2/14/14**