Checklist of E/OHS Activities for Facilities Safety Management and Fire Safety in Schools

Program Contact Person: Mike Siemer

Is the Facilities Safety Management program in place?  Yes  No

Does this school use contracted services for the Management Assistant Program? Yes No N/A

If no, who is the designated person or persons?

Fire and Life Safety in Schools

Program Contact Person: Mike Siemer

Is the Fire Marshal approved Emergency Evacuation Plan in place for each district building?  Yes  No

Most recent date of sprinkler electronics inspection: July, 2013_  N/A

Most recent date of alarm inspection: July, 2013 N/A

Most recent inspection of fire extinguishers: July, 2013 N/A

Most recent inspection of fume hoods with fire suppressant:  July, 2013__N/A

Are emergency lights tested at least monthly? Yes No N/A

Science safety Checklist completed? Yes No N/A

Has the Emergency Plan been updated for 2012-2013? Yes No N/A

Facilities Safety Review

Building: High School

| Mock-OSHA Review Area | Date Review Completed | N/A | Recommendations |
| --- | --- | --- | --- |
| Art | 12-17-10 |  |  |
| Dark Room |  | X |  |
| Wood Shop | 12-17-10 |  |  |
| Kitchen | 12-17-10 |  |  |
| Metal Shop | 12-17-10 |  |  |
| Halls, Gym, etc. | 12-17-10 |  |  |
| Graphic Arts | N/A | X |  |
| Maintenance/ Custodial | 12-17-10 |  |  |
| Transportation |  | X |  |
| Grounds/Garage | 12-17-10 |  |  |
| Chemistry/Life Science | 12-17-10 |  |  |

Fire and Life Safety Checklist

ART

X	Emergency phone numbers posted and MSDS available

X	Flammable liquids and combustibles stored properly

COMPRESSED GAS

X	Cylinders chained in place so they cannot fall over

X	Valve covers in place when cylinder not in use

SPRAY BOOTH

X	Fire control sprinkler heads kept clean

X	Mechanical ventilation provided when spraying is done in enclosed area

X	‘NO SMOKING’ signs posted in spray areas, paint rooms, booths, and storage

X	Spray area at least 20’ from flames, sparks, operating electrical motors

BOILER ROOM

X	Fire extinguisher mounted and accessible

X	No combustibles stored in boiler room

X	Two exits

CORRIDORS, ENTRANCES, STAIRS

X	All decorations, artwork in corridors limited to 25% of wall surface

X	All EXIT corridors and hallways free of obstructions

X	All EXIT doors open in the direction of exit without effort

X   All EXIT doors posted as exits with letters 5” high and ½” wide

X	All EXIT signs visible and with working lights, if lighted

X	Appropriate fire extinguishers are mounted within 75’ of outside areas containing flammable liquids and within 10’ of any inside storage area for such materials

X	Buildings over two levels have doors that close automatically in stair tower

X	Fire extinguishers free from obstruction or blockage

X	Fire extinguishers provided for the types of materials in the area where    used

Class A	Ordinary combustible material fires

Class B	Flammable liquid, gas, or grease fires

Class C	Energized-electrical equipment fires

X	Fire extinguishers serviced, maintained, and tagged every year

X	No dead-end corridor >20’

X	Non-exit doors, passages, and stairways labeled, “NOT AN EXIT”

X	Panic hardware on all exit doors and rooms with occupancy of 50 or more

X	Sprinkler heads protected by metal guards, when exposed to physical damage

ELECTRICAL

X	Extension cords used for permanent wiring

X	36” clear access to all electrical control panels for emergency shutdown

EXTERIOR

X	Dumpsters stored at least 5’ from any combustible buildings, doors, and windows

GYM

X	Stage curtain must be flame retardant

HOME EC

X	Outlets within 6’ of a water source must be GFC

KITCHEN

X	Exhaust hood, ducts, and filters clear of any grease accumulation

X	Fire extinguisher within 30’ of cooking equipment (min. 40BC)

X	Hood with auto fire extinguishing system inspected every 6 months

X	Means to shut off gas supply to the cooking equipment for emergency

X	MSDS available

X	Outlets within 6’ of a water source must be GFC

SCIENCE LABS

CHEMICALS

X	Chemicals stored in open lab work area kept to a minimum

X	Neutralizing chemicals and spill kits readily available

FIRE SAFETY

X	Aisles serving work areas on 2 sides at least 42” wide; those serving work   areas on one side only must be 36”

X	Flammable liquids stored in refrigerated equipment in closed containers

X	Flammable/combustible liquids and chemicals must not be stored in fume hoods or on the floor, except in original container

X	Refrigerators, freezers, or coolers that store or cool flammable liquids must be of explosion-proof construction and properly labeled

X	2A-20BC or larger rated fire extinguisher for each 3,000 feet of lab; travel distance must not exceed 50’ from anywhere in room

STORAGE

X	Acids stored in approved cabinets

X	Chemical storage area must have inventory

X	Chemical storage area properly ventilated

X	Chemicals properly labeled

X	Chemicals stored in approved containers (original shipping package)

X	Flammable liquids stored in approved cabinets

X	Shelves used for chemical storage should have lip or guard to prevent chemicals from falling off

X	Storage cabinets and rooms locked against unauthorized entry

VENTILATION

X	Hood tested every year

X	Lab hoods achieve 100 lfm

X	Means provided for manually shutting down ventilation equipment

STORAGE ROOMS

X	Room used for storage of combustibles must have 1-hour fire-rated walls (sheet rock or plaster) and fire-rated doors (or solid core 1.75” thick wood doors) with self-closer (or automatic fire sprinklers in them)

TECHNICAL LAB AREAS

X	Compressed gas cylinders (oxygen, acetylene, propane, etc.) secured so they cannot fall over

X	Emergency stop buttons colored red

X	Fire extinguishers located within 30’ of hazardous processes (painting, welding, and woodworking)—mounted and inspected

X	Flammable liquids stored in approved cabinets

X	Oil-soaked, greasy, or paint-soaked rags stored in metal containers with lids

X	Solvent wastes and flammable liquids are kept in fire-resistant, covered containers until they are removed from the worksite

X	Worksite clean and orderly with clear paths to exit

Completed by: _Brian Parrie   Date:12-17-2010