Facility Safety Review

Client Name: __Cedar Mountain High School- Morgan_____________________

                                                                                                                                                         OHSA fine Range

	Building
	Photo #
	Location
	Standard
	Description
	Minimum
	Maximum

	1966 Building
	1001, 1002
	Metal Shop
	Machine Guarding
	1/8in gap between grinding wheel and guard
	
	

	1966 Building
	1003
	Metal Shop
	Machine guarding
	Replace metal cutoff table
	
	

	1966 Building
	1004
	Metal Shop
	General Duty
	Mount fire blanket on wall
	
	

	1966 Building
	1005
	Metal Shop
	General Duty
	Welding and cutting masks stored in cabinet or hooks off floor
	
	

	1966 Building
	1006, 1007
	Wood Shop
	Electrical Code
	Protect power strip from saw dust or move miter saw
	
	

	1966 Building
	1008, 1016
	Hallway
	General duty
	Stair tread repair
	
	

	1966 Building
	1009
	Old locker Rm in basement
	Electrical Code
	Strap up and secure fire alarm wire
	
	

	1966 Building
	1010
	Basement Chemical storage
	General Duty
	Plaster delaminating Repair or remove
	
	

	1938 Building
	1011
	Laundry Room
	Chemical Safety
	Prevent laundry detergent from soaking floor
	
	

	1938 Building
	1012, 1013
	Laundry Room
	IAQ Mold
	Water Damage and Mold on wall remove sheetrock
	
	

	1938 Building
	1014
	Back Entrance
	General Maintenance
	Floor tile popping up and needs repair or replace
	
	

	Building
	Photo #
	Location
	Standard
	Description
	Minimum
	Maximum

	1938 Building
	1015
	Back Entrance
	General Maintenance 
	Door threshold not secured door move in frame.
	
	

	1966 Building
	1017
	Home Ec.
	General Duty
	Fasten table top down
	
	

	1966 Building
	1018,
1019
	Home Ec.
	General Duty
	Sewing table are unstable and unsafe. Replace
	
	

	 1966 Building                                                                                                                                                     
	1020,
1021
	Home Ec.
	Food Safety
	Counter tops delaminating repair or replace
	
	

	1966 Building
	1022, 1023
	Home Ec.

	Food Safety
	Under sink leaks repair and cabinet repair or replace
	
	

	1966 Building
	1024
	Gym Elevator

Second floor
	General Maintenance
	Floor tile coming up repair or replace
	
	

	1966 Building
	1025
	Boys Basement Locker Room
	IAQ
	HVAC ducting pulled down needs repair
	
	

	1966 Building
	1026,
1027
	Boys Basement Locker Room 
	Asbestos
Plumbing
	Water line pipe pulled down and needs repair
	
	

	1966 Building
	1028
	Boys basement lock room
	Electrical
	Open Electrical boxes need covered
	
	

	1966 Building
	1029,
1030
	Gym Boys Locker Room
	General Maintenance
	Replace fiberglass wall covering in shower
	
	

	1966 Building
	1031
	Preschool Room
	IAQ
	Replace unit vent
	
	

	1966 Building
	1032
	Stage
	General Duty
	Replace ceiling tile
	
	

	1938 Building
	1033
	Rm 206
	Electrical
	Replace end with grounded plug
	
	

	1966
	1034
	2nd floor hallway
	General maintenance
	Paint chipping off
Lead Paint?
	
	


Inspected by: __Brian Parrie_________________ Date:  3-20-2014___________
