Checklist of E/OHS Activities for Laboratory Standard/Chemical Hygiene Plan

Program Contact Person: Jeff Ehmke, CHO

Is the Laboratory Standard/Chemical Hygiene Plan in place? *Yes No N/A*

Is the Plan current?  *Yes No N/A*

Has the Plan been reviewed this school year? *Yes No N/A*

Fume hood was tested on: January 22, 2015.

 *(date)*

The results indicate air velocity to be: *satisfactory, unsatisfactory.*

Chemical inventory:

 Date of most recent survey: May, 2008

 Location of inventory listing: Chemistry Lab

Are Safety Data Sheets (SDSs) located with inventory? *Yes No N/A*

*Note: Intend to do a chemical sweep in the 2015-2016 school year. –EC-9/21/2015*

Are the SDS readily accessible? *Yes No N/A*

Has the DCFL Science Lab Checklist been completed? *Yes No N/A*

Is training for affected personnel complete? *Yes No N/A*

Date(s) of instruction: May, 2007

 Roster signed? *Yes No N/A*

Lesson plan outline available with roster? *Yes No N/A*

Status of Emergency Eye Wash/Deluge Shower:

 Is flushing conducted weekly? *Yes No N/A*

Is descriptive signage properly posted? *Yes No N/A*

Is flushing activity documented? *Yes No N/A*

# Fume Hood Evaluation

**Inspector : Brian Parrie** **Date 1/22/2015**

**Chemical Hygiene Officer: Jeff Ehmke**

**Hood #1** **Location: Room C-130**

|  |
| --- |
| **FIELD TEST (lft/min)** |
| 130 | 135 | 130 |
| 108 | 100 | 108 |

 Pass Fail (face velocity of 100 lf/min cannot be achieved)

Sash Height:15.5” low power, 20.5” high power

Used as Storage? *Yes No*

Clean? *Yes No*

Comments

**Completed by: Eileen Kirk**  **Date 1/22/15**