Checklist of E/OHS Activities for Laboratory Standard/Chemical Hygiene Plan

Program Contact Person: Amy Ruben			, CHO

Is the Laboratory Standard/Chemical Hygiene Plan in place?  Yes No N/A

Is the Plan current?  Yes No N/A

Has the Plan been reviewed this school year?  Yes No N/A

Fume hood was tested on _2/14/2013______________.

(date)

The results indicate air velocity to be: satisfactory, unsatisfactory.

Chemical inventory:

Date of most recent survey:  March 2, 2015

Location of inventory listing:  Chemistry lab

Are Safety Data Sheets (SDSs) located with inventory?  Yes No N/A

Are the SDS readily accessible?  Yes No N/A

Has the DCFL Science Lab Checklist been completed?  Yes No N/A

Is training for affected personnel complete?  Yes No N/A

Date(s) of instruction: 3/2/2015

Roster signed?  Yes No N/A

Lesson plan outline available with roster?  Yes No N/A

Status of Emergency Eye Wash/Deluge Shower:

Is flushing conducted weekly?  Yes No N/A

Is descriptive signage properly posted?  Yes No N/A

Is flushing activity documented?  Yes No N/A

Fume Hood Evaluation

Chemical Hygiene Officer: Amy Ruben

Hood: 	Location: ROOM 152

| FIELD TEST (lf/min) |  |  |
| --- | --- | --- |
| >100 lf/min | >100 lf/min | >100 lf/min |
| >100 lf/min | >100 lf/min | >100 lf/min |

X	Pass	Fail (face velocity of 100 lf/min cannot be achieved)

Sash Height: 24”

Used as Storage?  Yes  No

Clean?  Yes  No

Comments: This fume hood operated adequately when sash was in full open position.

Completed by: Brian Parrie	Date: 2/14/2013

Fume Hood Evaluation

Chemical Hygiene Officer: Amy Ruben

Hood: #1	Location: ROOM 152

| FIELD TEST (lf/min) |  |  |
| --- | --- | --- |
| >100 lf/min | >100 lf/min | >100 lf/min |
| >100 lf/min | >100 lf/min | >100 lf/min |

X	Pass		Fail (face velocity of 100 lf/min cannot be achieved)

Sash Height: Full open

Used as Storage?  Yes  No

Clean?  Yes  No

Comments: This fume hood operated adequately when sash was in full open position.

Completed by: Brian Parrie	Date: 2-14-13